## GRANTEE Variance Requests
Housing type
Date | Email Address | Grantee Representative Submitting Request: | DOE Project Officer | State/ Grantee | Relevant SWS (must include letter(s), e.g. 4.1103.1a) | SF | MH | MF | Proposed State Standard: | Difference between proposed standard and SWS: | Specific conditions where variance will apply: | Reasoning/Justification: | DOE Review Notes | Approved?
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | ASHRAE 62.2 2016 |  |  | X | An ASHRAE 62.2-2016 based ventilation strategy must be included in the audit report for all mid and high rise MF buildings, in addition to single family projects. When an audit report that indicates individual dwelling unit air sealing and/or window replacement is being proposed in buildings 4 stories or greater in height, or insufficient mechanical ventilation exists per the ASHRAE 62.2 2016 standard for this MF building type, but states ASHRAE 62.2-2016 cannot be fully implemented, it must indicate what efforts are to be undertaken to meet the standard to the greatest extent possible, and be submitted for review and approval prior to work beginning. 1. Existing Naturally Ventilated Multifamily Buildings: Existing naturally ventilated buildings 4 stories or greater in height, that do not carry out individual dwelling unit air sealing and/or window replacement will be exempt from the requirements of the ASHRAE 62.2-2016 Standard. Air sealing performed in common areas at the top and bottom of the building to address stack effect induced infiltration can still be carried out without having to provide additional ventilation. In those instances in which weatherization projects propose to include window replacement or perform other dwelling unit air sealing in the scope of work, the NYS WAP would require that ventilation be provided in accordance with ASHRAE 62.2-2016 to the greatest extent possible by incorporating mechanical ventilation into the window design. NYS WAP will address these buildings through the standard procedure provided. 2. Existing Mechanically Ventilated Buildings: NYS WAP will address these buildings through the standard procedure provided for improving existing central mechanical ventilation systems with respect to local code and the intent of the ASHRAE 62.2-2016 Ventilation Standard to the greatest extent possible, providing a pathway for achieving improved indoor air quality in the dwellings of these mechanically ventilated buildings undergoing weatherization. Subgrantees must include in their building project files copies of the latest NYS WAP ASHRAE calculator utilized to determine the building ventilation requirements, which can now account for any infiltration credits in horizontally attached multi-family units, for all their NYS WAP projects. In the event ASHRAE 62.2-2016 cannot be fully implemented the reasons why it cannot, or the efforts to implement it, must be documented in the project file, utilizing photos, test results, permit denials, etc., as well as explanatory commentary to justify the proposed project outcome that may not meet the formula driven ventilation requirement per the ASHRAE 62.2 2016 calculation. | Enshrine a standard procedure, applicable and repeatable state-wide, that addresses potential additional ventilation needs in both naturally ventilated, as well as existing mechanically (to any degree) ventilated large, vertically stacked multifamily buildings, while respecting local codes and the provisions of ASHRAE 62.2-2016, thereby providing a pathway for achieving improved indoor air quality as well as energy savings in these large buildings undergoing weatherization. | In all vertically stacked, naturally and / or mechanically ventilated Multifamily buildings 4 stories or greater in height | The last changes to the ASHRAE standard did not impact typical NYS WAP building types (SF, 2- 4 units and Manufactured Housing) and our approach to them. The change to the 2016 ASHRAE 62.2 standard that we were and are requesting a variance from is where vertically stacked multifamily buildings above 3 stories must also have in-unit ventilation strategies considered as part of their audit generated work scope. The building stock in NYS that the NYS WAP works in is traditionally among the oldest, if not the oldest, in this particular area (large, vertically stacked multifamily buildings). Addressing these often naturally ventilated, or partially mechanically ventilated, or fully mechanically ventilated (but over the course of a number of years, so there can be a mix of ventilation approaches in place), buildings in NYS poses unique, oftentimes expensive and complicated challenges when attempting to add and/or correct ventilation that meets the calculated QFAN required mechanical ventilation, or achieving anything close to a balanced system that improves on the existing IAQ and living conditions. Without a variance acknowledging a standard incorporating relief from having to meet the QFAN required mechanical ventilation in each of these project units would result in many of these post-war large multifamily buildings having to be deferred. Allowing for a NYS WAP standard that incorporates reviews of the audit and summary report by program staff, that includes a ventilation strategy prior to implementation , and requires justification of the ventilation approach in the project file, documenting the attempts made to meet the ASHRAE standard, would ideally prevent numerous project deferrals, cost overruns, and ineffective or detrimental ventilation strategies from being implemented, possibly causing inadvertent H&S issues or negative quality of life impacts for occupants. | The SWS Variance Request Process is not the mechanism by which ASHRAE variances are requested or supplied. ASHRAE is a programmatic requirement based on WPN 17-7 and is generally incorporated into the Energy Audit Approval Process and/or Annual Plan. DOE will take into consideration the documentation submitted and provide feedback and/or approval by means of a seperate Memo. | N/A
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 2.0201.2c | X | X |  | Verify that the ground outside the building slopes away from the foundation or that water doesn’t puddle near the foundation. Install or repair rain gutters and downspouts as necessary, verifying effective pitch, and that downspouts discharge at least 3 feet away from building. | In many NYS properties, a 6' minimum required length for a downspout's discharge is not feasible. | In NYS WAP SF & MH projects where it is necessary to address ground moisture reduction, prior to performing energy conservation measures in order to protect those measures, as well as improve the health & safety of the building and its occupants. | Before air sealing and insulating building components, exterior water management is addressed. Addressing ground source moisture has always been considered in NYS WAP prior to air sealing the floor of a SF project or insulating the belly of a manufactured home. NYS WAP believes requiring a 3' minimum discharge distance and assuring a ground slope away from the building reasonably addresses these building deterioration concerns and better reflects the reality of most NYS WAP project situations relative to limited lot space, close proximity to neighbors, propety line concerns and local issues regarding run off. Requiring a 3' minimum discharge distance instead of a 6' minimum discharge distance, and not requiring grading or landscaping activities in these typical scenarios will lessen the likelihood of project deferrals. It's been our experience in NYS, barring a serious landscape flaw, and it being past practice that NYS WAP subgrantees do not engage in making landscape modifications to properties beyond the removal of minor, natural vegetation to facilitate the performance of a measure, a slope away from the building and 3' of discharge distance is typically sufficient. If it is not, and there is no other viable alternative to addressing the ground moisture concerns, the project would have to be deferred. NYS WAP work can only proceed when it is clear that the work will not cause or be compromised by moisture problems. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 2.0201.3a | X | X |  | Verify that the ground outside the building slopes away from the foundation or that water doesn’t puddle near the foundation. Install or repair rain gutters and downspouts as necessary, verifying effective pitch, and that downspouts discharge at least 3 feet away from building. | NYS WAP subgrantees do not engage in performing signifcant modifications to the landscape, like changing the existing grade of the lot 6" every 10'. | In NYS WAP SF & MH projects where it is necessary to address ground moisture reduction, prior to performing energy conservation measures in order to protect those measures, as well as improve the health & safety of the building and its occupants. | Before air sealing and insulating building components, exterior water management is addressed. Addressing ground source moisture has always been considered in NYS WAP prior to air sealing the floor of a SF project or insulating the belly of a manufactured home. NYS WAP believes requiring a 3' minimum discharge distance and assuring a ground slope away from the building reasonably addresses these building deterioration concerns and better reflects the reality of most NYS WAP project situations relative to limited lot space, close proximity to neighbors, propety line concerns and local issues regarding run off. Requiring a 3' minimum discharge distance instead of a 6' minimum discharge distance, and not requiring grading or landscaping activities in these typical scenarios will lessen the likelihood of project deferrals. It's been our experience in NYS, barring a serious landscape flaw, and it being past practice that NYS WAP subgrantees do not engage in making landscape modifications to properties beyond the removal of minor, natural vegetation to facilitate the performance of a measure, a slope away from the building and 3' of discharge distance is typically sufficient. If it is not, and there is no other viable alternative to addressing the ground moisture concerns, the project would have to be deferred. NYS WAP work can only proceed when it is clear that the work will not cause or be compromised by moisture problems. | Approved 8/26/21 Note: The SWS is not a prescriptive standard. The SWS is an objective based standard which describes the outcomes of measure installed if selected by the energy audit procedures as developed by the Grantee. The proposed standard meets the desired outcome of this specification and can be approved. | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 2.0201.3b | X | X |  | Verify that the ground outside the building slopes away from the foundation or that water doesn’t puddle near the foundation. Install or repair rain gutters and downspouts as necessary, verifying effective pitch, and that downspouts discharge at least 3 feet away from building. Remove minor, natural vegetation (that which has grown naturally, without human aid, and has been left undisturbed for some time) which may be impeding drainage | SWS states: "With occupant approval: Clear all vegetation within 3' of the home or trim all landscaping so that it is at least 1' away from the home". NYS WAP subgrantees do not engage in performing landscape modifications, such as cutting or removing existing vegetation on any properties, beyond the removal of minor natural growth impeding the performance of a measure. | In NYS WAP SF & MH projects where it is necessary to address ground moisture reduction, prior to performing energy conservation measures in order to protect those measures, as well as improve the health & safety of the building and its occupants. | Before air sealing and insulating building components, exterior water management is addressed. Addressing ground source moisture has always been considered in NYS WAP prior to air sealing the floor of a SF project or insulating the belly of a manufactured home. NYS WAP believes requiring a 3' minimum discharge distance and assuring a ground slope away from the building reasonably addresses these building deterioration concerns and better reflects the reality of most NYS WAP project situations relative to limited lot space, close proximity to neighbors, propety line concerns and local issues regarding run off. Requiring a 3' minimum discharge distance instead of a 6' minimum discharge distance, and not requiring grading or landscaping activities in these typical scenarios will lessen the likelihood of project deferrals. In NYS, the occupant of a MH is not necessarily the owner of the lot or existing landscaping. It's been our experience in NYS, barring a serious landscape flaw, and it being past practice that NYS WAP subgrantees do not engage in making landscape modifications to properties beyond the removal of minor, natural vegetation to facilitate the performance of a measure, a slope away from the building and 3' of discharge distance is typically sufficient. If it is not, and there is no other viable alternative to addressing the ground moisture concerns, the project would have to be deferred. NYS WAP work can only proceed when it is clear that the work will not cause or be compromised by moisture problems. | Approved 8/26/21 Note: The SWS is not a prescriptive standard. The SWS is an objective based standard which describes the outcomes of measure installed if selected by the energy audit procedures as developed by the Grantee. The proposed standard meets the desired outcome of this specification and can be approved. | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 3.0103.1f | X | X | X | In situations where head space is limited at an interior hatch opening (ex. a sloped roof where headroom is very low at the hatch and a rigid insulation dam would bar future access or interfere w/ hatch functioning) fiberglass batts be used to construct a low profile insulation dam. | NYS WAP would allow for use of a 'non-rigid' material (fiberglass batts) to construct a surrounding baffle as needed. | In NYS WAP projects whenever loose fill insulation has been installed in an attic and the space available for the interior access hatch to open is limited for Weatherization purposes. | The procedure and best practices traditonally followed in the NYS WAP are in agreement with the SWS, however the SWS doesn't specifically address a situation where head space is limited for an interior attic hatch, which will occur in NYS WAP housing stock. This variance keeps NYS WAP in alignment with the SWS, while allowing flexibility for meeting the stated objectives ( i.e. - achieve uniform R-value on the attic door or hatch, achieve uniform R-value on the attic floor and prevent loose attic floor insulation from entering the living area), in a very specific, limited but recurring project scenario. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 4.0202.1c | X | X | X | Based on accessibility and construction, install non-rigid or rigid blocking material, to be made airtight, at all cavity openings that align with the pressure boundary and will not fail under dense pack pressures | NYS WAP would also allow for the use of non-rigid (ex. fiberglass insulation) to be used to completely stuff the cavity opening, which is then made airtight with the application of SPF. | All enclosed wall cavity situations where dense pack insulation is being performed. | Based on age of construction and accessibility to cavity openings, requiring the use of rigid material that needs to be cut to size per cavity opening can be burdensome and untimely, particularly when working in attics, given the likelihood of cavity openings not being uniform. NYS WAP would allow for the use of non-rigid (ex. fiberglass insulation) to be used to completely fill the cavity opening, which would then be made airtight with an application of SPF to seal the cavity opening. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 4.0202.1g | X | X | X | Interior installation holes will be coated, patched and properly sealed to paint ready condition; All construction debris and dust will be collected and removed, leaving work area in 'broom clean' condition. | SWS states: Interior holes will be coated and patched to match original interior surface characteristics; NYS WAP proposal includes the requirement for proper patching but does not require matching 'original interior surface characteristics' using program funds. | All interior surfaces where holes were drilled for insulating / weatherization purposes. | It is not time efficient nor cost effective for a sub-grantee to attempt to match 'original interior surface characteristics' of each hole drilled for installation purposes; requiring all interior holes to be properly coated, patched and effectively sealed to paint ready condition ensures the dwelling has been returned to an airtight and clean condition, and ensures future work can be done easily and successfully. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 4.0388.1d |  | X |  | Verify that the ground outside the MH is free of obstructions that may preclude the installation of effective foundation skirting. If obstructions exist that are non-permanent and do not pose a danger to the subgrantee, safely remove them. Remove minor, natural vegetation (that which has grown naturally, without human aid, and has been left undisturbed for some time) which may be impeding installation. If there is landscaping / cultivated vegetation in the installation area that would require removal, notify the owner they would need to remediate the situation prior to installation occurring. | NYS WAP subgrantees do not engage in performing landscape modifications, such as cutting or removing existing vegetation on any properties, beyond the removal of minor natural growth impeding the performance of a measure. | In all NYS WAP MH projects where foundation skirting or 'belly work' is a component of the workscope and removal of 'existing vegetation' may be beyond that of simple weed or brush removal. | NYS WAP subgrantees do not engage in performing landscape modifications, such as cutting or removing existing vegetation on any properties, beyond the removal of minor natural growth impeding the performance of a measure, even with the 'client's approval' for their and the program's protection. Many MH project clients are not the owners of the lot on which landscaping or plantings may have been done, nor do they know what is 'permanent' and what isn't. NYS WAP feels it is inadvisable to require the subgrantee to be involved in this activity, beyond the conditions cited, and it should be performed by the owner when necessary to facilitate the success of the project and protect the subgrantee from any future claims. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 5.0101.1b | X | X | X | If you are to replace the existing thermostat as a part of weatherization work, discuss programmable thermostats with occupants. If they can use a programmable thermostat effectively, then install one that correctly matches the existing, or the to be installed, system. Educate occupants on the use of the thermostat and leave a copy of manufacturer’s directions with them. | Doesn't require the installation of a double setback programmable thermostat if the auditor determines it wouldn't be an energy saving expenditure. | In all NYS WAP projects where thermostat replacement is a component of the workscope and the residents may not have the ability, or desire, to utilize a programmable thermostat as required. | A programmable thermostat can be a big energy saver if the building’s occupants understand how to program it effectively and have the ability and desire to utilize it effectively, as prescribed. However, if they don't, the cost won't be justified. Also, a programmable thermostat won’t save any energy if occupants already control day and night temperatures effectively. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 5.0201.1b | X | X | X | If you are to replace the existing thermostat as a part of weatherization work, discuss programmable thermostats with occupants. If they can use a programmable thermostat effectively, then install one that correctly matches the existing, or the to be installed, system. Educate occupants on the use of the thermostat and leave a copy of manufacturer’s directions with them. | Doesn't require the installation of a double setback programmable thermostat if the auditor determines it wouldn't be an energy saving expenditure. | In all NYS WAP projects where thermostat replacement is a component of the workscope and the residents may not have the ability, or desire, to utilize a programmable thermostat as required. | A programmable thermostat can be a big energy saver if the building’s occupants understand how to program it effectively and have the ability and desire to utilize it effectively, as prescribed. However, if they don't, the cost won't be justified. Also, a programmable thermostat won’t save any energy if occupants already control day and night temperatures effectively. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 7.0302.1e | X | X | X | Provide for an adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations; Install appliance and plumbing to allow for inspection, maintenance, and replacement of the appliance and its components, without disturbing other installed equipment, controls, piping, and components, other than what requires repair/replacement; Ensure that anode rod is accessible for replacement | SWS states: Provide a level working space not less than 30" in length and 30" in width in front of the control side of the appliance; NYS WAP: Provide adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations. | Throughout NYS in all Weatherization Assistance Program projects. | NYS WAP does not see the beneifit of mandating subgrantees to possibly engage in construction modifications in our older housing stock that could lead to larger issues, i.e. disturbing other plumbing, piping, appliance controls, etc. , in order to meet a specific 30" by 30" level working space requirement in every instance. Requiring the subgrantee to provide adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations, should be sufficient to be reasonably assured the appliance can be easily maintained and replaced when the time comes, which we feel is the desired outcome and goal of the specification. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 7.0302.2 | X | X | X | Provide for an adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations; Install appliance and plumbing to allow for inspection, maintenance, and replacement of the appliance and its components, without disturbing other installed equipment, controls, piping, and components, other than what requires repair/replacement; Ensure that anode rod is accessible for replacement | SWS states: Provide a level working space not less than 30" in length and 30" in width in front of the control side of the appliance; NYS WAP: Provide adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations. | Throughout NYS in all Weatherization Assistance Program projects. | NYS WAP does not see the beneifit of mandating subgrantees to possibly engage in construction modifications in our older housing stock that could lead to larger issues, i.e. disturbing other plumbing, piping, appliance controls, etc. , in order to meet a specific 30" by 30" level working space requirement in every instance. Requiring the subgrantee to provide adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations, should be sufficient to be reasonably assured the appliance can be easily maintained and replaced when the time comes, which we feel is the desired outcome and goal of the specification. | Approved 8/26/21 | Yes
2021-06-16 | kevin.oconnell@nyshcr.org | K. O'Connell | M. Peterson | NY | 7.0302.3 | X | X | X | Provide for an adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations; Install appliance and plumbing to allow for inspection, maintenance, and replacement of the appliance and its components, without disturbing other installed equipment, controls, piping, and components, other than what requires repair/replacement; Ensure that anode rod is accessible for replacement | SWS states: Provide a level working space not less than 30" in length and 30" in width in front of the control side of the appliance; NYS WAP: Provide adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations. | Throughout NYS in all Weatherization Assistance Program projects. | NYS WAP does not see the beneifit of mandating subgrantees to possibly engage in construction modifications in our older housing stock that could lead to larger issues, i.e. disturbing other plumbing, piping, appliance controls, etc. , in order to meet a specific 30" by 30" level working space requirement in every instance. Requiring the subgrantee to provide adequate working space in front of the control side of the appliance, following manufacturer's service space recommendations, should be sufficient to be reasonably assured the appliance can be easily maintained and replaced when the time comes, which we feel is the desired outcome and goal of the specification. | Approved 8/26/21 | Yes